Maeser Ridge Medical Center, CT-2 status
Jenn Fowler, 8/10/26

Writing this one properly because I want a record of it somewhere other
than my head.

Today the CT-2 dipslide came back 10^5. The sequence since late May reads
like a staircase: 10^4 on 5/25, 10^4 through most of June and July, 10^5 on
7/27, back to 10^4, and now 10^5 again. Our treatment guidelines are clear
about what consecutive counts at or above 10^4 mean at a healthcare
facility: notify operations leadership within one business day, shock dose,
and schedule remediation. The shock doses happen because I do them at every
visit. The rest has not happened.

What this tower needs, and has needed since June:
1. Offline mechanical clean and disinfection of fill and basin.
2. Replacement of the bromine feed assembly, not another injector cleaning.
3. A documented retest sequence afterward.

I have told hospital maintenance (Gary, twice in person, and their chief
engineer on 7/13) and I have raised it in our shop three times since June.
Everyone agrees and nothing gets scheduled. This is a hospital. The tower
sits over the loading dock where the air intake for the east wing is not
far away. If this ever turns into a real problem the first question will be
"you knew since May?"

I am putting it in front of Dana on Monday and I am not letting it drop
this time.