SITE NOTE - Pintura Polymers, Springville
Marcus Webb, 7/21/26 (ahead of 7/22 service)

Status of the loop water loss (WO-0139, opened 6/12, still open).

Where things stand:
1. Makeup meter 45,600 as of 7/22. The loop is still taking roughly 400
   gallons a day. Nitrite keeps burning down into the 400s and 500s between
   visits no matter how hard we dose.
2. CL-40 used at this site since March is more than some accounts use in two
   years. At current pace this one loop will empty a drum roughly every
   month. That is chemical cost on their invoice and drum count out of our
   warehouse.
3. Iron in the loop is up over 1 ppm. Fresh aerated makeup is chewing on the
   system. The longer this runs the more of the piping we lose.
4. Customer side: plant engineer agrees it is probably the buried section
   near the loading dock. The excavation quote is sitting in their capital
   review. Nobody owns pushing it.

Recommendation: someone above my pay grade should call their plant manager
and put a date on the leak locate. Keeping the loop dosed is a bandage, not
a plan. If they wait until winter and that line lets go under the dock we
will be having a very different conversation.